Delhi Fire Service

Procedure for obtaining NOC from fire department (prior to commencement of construction activities)

- The following buildings are required to obtain clearance from Delhi Fire Service (DFS):

(1) Residential buildings (other than hotels and guest houses) having height more than 15 meters or having ground plus four upper stories including mezzanine floor.

(2) Hotels and guest houses having height more than 12 meters having ground plus three upper stories including mezzanine floor.

(3) Educational buildings having height more than 9 meters or having ground plus two upper stories including mezzanine floor.

(4) Institutional buildings having height more than 9 meters or having ground plus two upper stories including mezzanine floor.

(5) All Assembly buildings.

(6) Business buildings having height more than 15 meters or having ground plus four upper stories including mezzanine floor.

(7)  Mercantile buildings having height more than 9 meters or having ground plus two upper stories including mezzanine floor.

(8) Industrial buildings having covered area on all floors more than 250 square meters.

(9) Storage buildings having covered area on all floors more than 250 square meters.

(10) All Hazardous buildings having covered area on all floors more than 100 square meters.

(11) Underground Structures.

- Building plans of aforesaid buildings shall be submitted to Local authority i.e. MCD, NDMC, DDA etc. who after their scrutiny, forward the plans to DFS as per clause 2.8 of Unified Building Bye Laws (UBBL) 2016 along with duly filled common application form (CAF). The said clause states that "The building plans for buildings covered under Rule 27 of Delhi Fire Service Rules shall be marked fire and life safety measures as per the National Building Code of India concerning minimum standards for fire prevention and fire protection as covered under Rule 33 of the Delhi Fire Service Rules as amended from time to time; unless otherwise specified in these bye laws". However, the cases of government buildings can directly be submitted under simplified procedure as per clause 3.1.3 of UBBL 2016.

- The format of CAF is as under:

| S. No | Field Name | Type | Data Type | Max. Length | Validation ID |
| --- | --- | --- | --- | --- | --- |
|  | Division | *Drop Down | As per current form | NA | Val1 |
|  | Type of Occupancy (As per clause 1.4.75 of UBBL 2016 ) | *Textbox field | String | 16 | Val1 |
|  | Height of the building (In meters) | *Textbox field | Number , Decimal up to two digit | 3 | Val1 |
|  | Number of floors | *Textbox field | Numeric | 3 | Val1 |
|  | Covered area at ground floor (In Sq mt.) | *Textbox field | Numeric | 7 | Val1 |
|  | Typical floor area (In Sq mt.) | *Textbox field | Numeric (decimal up to two digit) | 7 | Val1 |
|  | No. of basement | *Textbox field | Numeric | 2 | Val1 |
|  | Basement floor area (In Sq mt.) | *Textbox field | Numeric (decimal up to two digit) | 7 | Val1 |
|  | Total covered area on all floor (including stilt and basements) (In Sq mt.) | *Textbox field | Numeric (decimal up to two digit) | 10 | Val1 |
|  | Access to building (As per clause 8.2/7.13.3 of UBBL 2016) - Road width (In meter) - Gate width (In meter) - Width of Internal Road (In meter) - Distance of the internal road from building line (In meter). - Remarks (if any) | Heading *Textbox field *Textbox field *Textbox field *Textbox field Text area | Numeric Numeric Numeric Numeric String | 4 4 4 4 200 | Val1 |
|  | Number,width,type & arrangement of exits(As per clause 7.8 of UBBL 2016) - Travel distance (In meter) - Dead end travel distance (In meter) No of Staircases(As per clause 7.10.1 of UBBL 2016) - Upper floors - Basements Width of staircase (As per clause 8.4.3 of UBBL 2016) - Upper floor (In meter) - Basement (In meter) | Heading *Textbox field *Textbox field Heading *Textbox field *Textbox field Heading *Textbox field *Textbox field | Numeric Numeric Numeric Numeric Numeric Numeric | 4 4 4 4 4 4 | Val1 |
|  | - Provision of Staircase (As per clause 7.11 of UBBL 2016) | *Radio Button | Yes/No | NA | Val1 |
|  | - Fire Tower (As per clause 1.4.46 /9.3.13 of UBBL 2016) - No. of continuous staircases to terrace. (As per clause 7.11(m) of UBBL 2016) - Ramp if any(width in meter) (As per clause 8.4.7 of UBBL 2016) | * Radio Button *Textbox field *Textbox field | Yes/No Numeric Numeric | NA 4 4 | Val1 |
|  | Protection of Exits (As per clause 7.5 of UBBL 2016) - Fire Check door. (As per clause 8.4.5 (c)of UBBL 2016) - Pressurization. (As per clause 9.3.2 of UBBL 2016) - Width of Corridor (In meter)(As per clause 7.11.2 & 8.4.8 of UBBL 2016) - Door Size (In meter) (As per clause 7.12/7.23of UBBL 2016) - Remarks if any | Heading * Radio Button * Radio Button *Textbox field *Textbox(width)*Textbox(height) Text area | Yes/No Yes/No Numeric Numeric * Numeric String | NA NA 4 4 *4 200 | Val1 |
|  | Compartmentation(As per clause 8.4.6 of UBBL 2016) - Compartment size (Area in Sq mt.) - No of fire compartments at upper floor - No of fire compartments at Basement Level - Type of Compartmentation - By Fire resisting wall of 02 hrs rating - By Fire curtain of 02 hrs rating - By water curtain - Fire Dampers V Fire check door | Heading *Textbox field *Textbox field *Textbox field * Radio Button * Radio Button * Radio Button * Radio Button * Radio Button | Numeric Numeric Numeric Yes/No Yes/No Yes/No Yes/No Yes/No | 4 4 4 NA NA NA NA NA | Val1 |
|  | Smoke Management System - Mechanical / Natural - Basement air changes (12 ACPH) - Upper floors air changes (12 ACPH) - Fresh air supply at bottom level - Exhaust air discharge at ceiling level - Provision of fresh air cut outs - Provision of exhaust air cut outs - Ventilation calculations with drawing - Remarks, if any | Heading *Text Box * Radio button * Radio button * Radio button * Radio button * Radio button * Radio button * Radio Button Text area | String Yes/No Yes/No Yes/No Yes/No Yes/No Yes/No Yes/No String | 13 NA NA NA NA NA NA NA 200 | Val1 |
|  | Fire Extinguishers {As per clause 9.3.9 of UBBL 2016& (IS 2190)} - Total numbers on each floor - Remarks, if any | Heading *Text Box Text area | Numeric String | 4 200 | Val1 |
|  | First-aid hose reels {As per clause 9.3.9 of UBBL 2016} - Location near stairs - Total no of each floor. - Remarks | Heading * Radio Button *Text Box Text area | Yes/No Numeric String | NA 4 200 | Val1 |
|  | Automatic fire detection and alarming system {As per clause 9.3.9 of UBBL 2016& (IS 2189) } - Type of detectors - Detector above false ceiling - Provision of detectors in duct, shaft etc. - Remarks, if any | *Textbox * Radio Button * Radio Button Text area | String Yes/No Yes/No String | 10 NA NA 200 | Val1 |
|  | Manually operated electric fire alarm (MOEFA) (As per clause 9.3.9 of UBBL 2016) | * Radio Button | Yes/No | NA | Val1 |
|  | Public address system (As per clause 9.3.9 of UBBL 2016) | * Radio Button | Yes/No | NA | Val1 |
|  | Automatic sprinkler system(As per clause 9.3.9 of UBBL 2016 & IS 15105) - Total no of sprinkler head in one installation (approx.) as per IS-15105. - Basement - Upper floor - Sprinkler above false ceiling. - Calculation as per IS 15105 with drawings - Fire service inlet | Header *Textbox *Textbox *Textbox * Radio Button * Radio Button * Radio Button | Numeric Numeric Numeric Yes/No Yes/No Yes/No | 4 4 4 NA NA NA | Val1 |
|  | Internal hydrants (As per IS 3844 ) - Size of riser/down comer (in mm) - Number of hydrants per floor - Location near to staircase - Hose boxes near each landing valve - Fire services inlet - Remarks | Header *Textbox *Textbox * Radio Button * Radio Button * Radio Button Text area | Numeric Numeric Yes/No Yes/No Yes/No String | 3 3 NA NA NA 200 | Val1 |
|  | Yard hydrants as per IS 13039 - Total no of yard hydrants - Distance between two yard hydrants (in meter) - Number of hose box - Remarks | Header(label) *textbox *textbox *textbox Text area | Numeric Numeric Numeric String | 4 4 4 200 | Val1 |
|  | Pumping Arrangements (As per clause 9.3.9 of UBBL 2016) - Ground level - Location of pump room - Discharge of main pump (liter per minute). - Head of main pump (in meter) - Number of main pumps - Jockey pump output (LPM) - Jockey pump head (in meter) - Number of Jockey Pumps - Standby pump output (LPM) - Standby pump head (in meter) - Direct access to pump house from ground level - Terrace Level - Discharge of pump (LPM) - Head of the pump (In meter) - Remark if any | Header(label) Label *Textbox *Text Box *Text Box *Text Box *Text Box *Text Box *Text Box *Text Box *Text Box * Radio Button Label *Text box *Text box Text area | String Numeric Numeric Numeric Numeric Numeric Numeric Numeric Numeric Yes/No Label Numeric Numeric String | 10 4 4 4 4 4 4 4 4 NA 4 4 200 | Val1 |
|  | Captive water storage for firefighting (As per clause 9.3.9of UBBL 2016& IS 15105) - Location of underground tank - Underground tank capacity (In Liters) - Draw off connection - Fire Service Inlet - Access to tank - Overhead tank capacity (In Liters) - Ladder for inspection (As per clause 7.10.3 of UBBL 2016) - Cross section drawing of tanks - Remarks, if any | Header(label) *Text Box *Text Box * Radio Button * Radio Button * Radio Button *Text Box * Radio Button * Radio Button Text area | String Numeric Yes/No Yes/No Yes/No Numeric Yes/No Yes/No String | 10 8 NA NA NA 8 NA NA 200 | Val1 |
|  | Exit Signage (As per clause 7.11 (r) of UBBL 2016) | * Radio Button | Yes/No | NA | Val1 |
|  | Provision of lifts (As per clause 8.4.4/9.3.3 of UBBL 2016) - No of passenger lifts - No of car lifts - No. of fire lifts - Fireman’s grounding switch - Pressurization of lift shaft. (As per clause 8.4.4 m of UBBL 2016) - Pressurization of lift lobby. (As per clause 8.4.4 m of UBBL 2016) - Remarks, if Any | Header(label) *Text Box *Text Box *Text Box * Radio Button * Radio Button Radio Button Text area | Numeric Numeric Numeric Yes/No Yes/No Yes/No String | 4 4 4 NA NA na 200 | Val1 |
|  | Standby power supply (As per clause 8.5.3 of UBBL 2016) | * Radio Button | Yes/No | NA | Val1 |
|  | Refuge Area (As per clause 9.3.6/ 9.3.7 of UBBL 2016) - Levels/ floors - Area at each Level (In sq mt.) - Direct access to nearest staircase - Fire check floor (As per clause 9.3.8 of UBBL 2016) - Remarks | Header(label) *Textbox field *Textbox field * Radio Button * Radio Button Text area | All allowed All allowed Yes/No Yes/No String | 50 50 NA NA 200 | Val1 |
|  | Fire control room ( 9.3.10/ 9.3.14 of UBBL 2016) - Location near main entrance at ground floor - Provision of fire safety officer (9.3.14 of UBBL 2016) - Remarks(if any) | Header(label) * Radio Button * Radio Button Text area | yes/no yes/no String | NA NA 200 | Val1 |
|  | Special fire protection systems for protection of special risks, if any (special risks-transformer, electrical panel, petroleum products, boiler room etc.) | *Text area | As per current form |  | As per current form |

- The building plans shall include 02 sets of architectural plans duly marked with fire and life safety systems, section, elevation, key plan, layout plan, 01 set of Automatic Sprinkler system plans along with calculations as per IS 15105, 01 set of smoke management plans along with calculations as per NBC part 4 as prescribed under rule 33 of DFS rules 2010.

- The fire and life safety provisions stipulated under rule 33 of DFS rules 2010 are the minimum standards for fire prevention and fire safety for buildings as may be applicable with reference to the height of the building and class of occupancy, provided in the building bye-laws or National Building Code of India 2005 relating to the following matters:-

(1) Access to building

(2) Number, Width, Type and Arrangement of exits

(3)Protection of Exits by means of fire check door (s) and or pressurization.

(4) Compartmentation.

(5) Smoke Management System.

(6) Fire Extinguishers.

(7) First-Aid Hose Reels.

(8) Automatic fire detection and alarming system.

(9) MOEFA.

(10) Public Address System.

(11) Automatic Sprinkler System.

(12) Internal Hydrants and Yard Hydrants.

(13) Pumping Arrangements.

(14) Captive Water Storage for fire fighting.

(15) Exit Signage.

(16) Provision of Lifts.

(17) Standby power supply

(18) Refuge Area.

(19) Fire Control Room

(20) Special Fire Protection Systems for Protection of special risks,:

Provided that classes of occupancies or buildings or premises for which fire prevention and fire safety measures are not provided in the building bye-laws or National Building Code of India 2005, the Director may require owner or occupier of such occupancies or buildings or premises to provide fire prevention and fire safety measures in accordance with international standards.

- The building plans are examined by Fire Prevention Wing of DFS in accordance with the provisions of UBBL 2016/National Building Code of India and International Codes for issuance of construction permit. The observations are conveyed to concerned local authority. If they are found to be in accordance with the statutory requirements. One set of buildings plans duly signed are returned to local authority.

Comprehensive list of Documents to be submitted

- Reference letter from local authority

- In case of government buildings , a copy of approved layout plan with letter of competent authority

- 02 sets of key and layout plan

- 02 sets of architectural plans duly marked with fire and life safety systems

- 02 sets of Section & Elevation

- 02 sets of Automatic sprinkler system drawings alongwith calculations as per IS 15105, wherever required.

- 02 sets of smoke management drawings, lift / staircase pressurization, along with calculations as per NBC, wherever required.